## 1. Introduction
Data Center Power and Cooling Requirements Calculator
The data center's power, cooling and standby power supply must be able to adequately support current and future needs. Whether IT is building, refreshing, or moving the data center, it is important to understand these requirements. Accurate estimates of facility requirements are a critical input to the project’s final budget. Once the load estimate has been determined, IT should seek professional expertise as data center construction requires specialized skills. This tool can be used to determine a high level estimation for the data center's power, cooling, and standby power requirements within a range of 10%-15% accuracy. Complete the white cells with required information and follow the arrows to determine final results. Note: Some calculations in this tool are adapted from APC information.
Info-Tech Research Group tools and template documents are provided for the free and unrestricted use of subscribers to Info-Tech Research
Group services. These documents are intended to supply general information only, not specific professional or personal advice, and are not
intended to be used as a substitute for any kind of professional advice. Use this document either in whole or in part as a basis and guide for
document creation. To customize this document with corporate marks and titles, simply replace the Info-Tech Information in the Header and
Footer fields of this document.
Start Calculator

## 2. Required Inputs
Required Inputs |  | Next Step >>>
Enter the required information into the white cells below and click on the "Next Step" buttons to continue through the calculator.
Input Table
Item | Number
Total floor area in the data center (sq. ft) | 1200
Enter anticipated number of future servers to be added. | 50
Which cooling device is used in the data center? (select from drop down). | DX System
Enter the three phase AC voltage provided at the service entrance. (kW) | 240
Maximum number of people in the data center? (People that will be consistently working within the data center. A maximum number should be used to account for intermittent personnel and air exchange.) | 5
Power distribution rating (Watts)? (Total power drawn from the power distribution unit in Watts.) | 191

## 3. Server Load Calculations
Existing Server Load Calculations | [8 empty] | Next Step >>>
Enter server information, along with Amps and Volts into the table below to calculate the total server load in kW for the organization. Where a power utility or calculation tool is not available from the vendor to express power requirements as kW, nameplate ratings are used to arrive at a kW input. This tool uses the following formula for this conversion: VOLT AMPS = AMPS x VOLTS WATTS = VOLT AMPS x 0.67 kW = WATTS/1000 List each server located in the data center in the table below. Use nameplate ratings to collect amps and volts for each device to determine the kW required. Be sure to include the device name for tracking purposes.
Inputs | [5 empty] | Outputs
Device Name | Server Model | Utilization Assumption | AMPS | VOLTS | WATTS (Enter if volts and amps are not available) | WATTS | kW | Total Existing Server Load (kW)
IT_NETPRO | PROLIANT DL 360 G4p | 30-70% | 1.2 | 240 |  | 192.96 | 0.19296 | 78.7928
IT_SURFWATCH | PROLIANT DL 360 G2 | 30-70% | 5 | 48 |  | 160.8 | 0.1608
PRD_CITRIX02 | PROLIANT BL 20P G2 | 30-70% |  |  | 684 | 684 | 0.684
PRD_CITRIX03 | PROLIANT BL 20P G2 | 30-70% |  |  | 684 | 684 | 0.684 | Average Server Load (kW)
PRD_CITRIX01 | PROLIANT BL 20P G2 | 30-70% |  |  | 684 | 684 | 0.684
PRD_CITRIX04 | PROLIANT DL 360 G4p | 30-70% |  |  | 336 | 336 | 0.336 | 0.90566
IT_DEVELOPMENT1 | PROLIANT DL 320 G2 | 30-70% |  |  | 251 | 251 | 0.251
IT_REMOTEACCESS | PROLIANT DL 320 G2 | 30-70% |  |  | 251 | 251 | 0.251
IT_SOURCESAFE | PROLIANT DL 320 G2 | 30-70% |  |  | 251 | 251 | 0.251
IT_BESDMZ | PROLIANT DL 320 G2 | 30-70% |  |  | 251 | 251 | 0.251
IT_AVTECH | PROLIANT DL 320 G2 | 30-70% |  |  | 251 | 251 | 0.251
IT_SYNCSORT | PROLIANT DL 320 | 30-70% |  |  | 171 | 171 | 0.171
PRD_MOBILEAPPS | PROLIANT DL 320 G2 | 30-70% |  |  | 251 | 251 | 0.251
PRD_ANTGY | PROLIANT DL 320 G5 | 30-70% |  |  | 194 | 194 | 0.194
PRD_ACCOUNTFND | PROLIANT DL 360 G2 | 30-70% |  |  | 267 | 267 | 0.267
PRD_SCHEDULELEADS | PROLIANT DL 360 G2 | 30-70% |  |  | 267 | 267 | 0.267
IT_SURFWATCH | PROLIANT DL 360 G2 | 30-70% |  |  | 267 | 267 | 0.267
IT_EDIRECTORY | PROLIANT DL 360 G2 | 30-70% |  |  | 267 | 267 | 0.267
PRD_FAS1 | PROLIANT DL 360 G3 | 30-70% |  |  | 373 | 373 | 0.373
PRD_BES1 | PROLIANT DL 360 G5 | 30-70% |  |  | 481 | 481 | 0.481
IT_LDDHCP1 | PROLIANT DL 360 G3 | 30-70% |  |  | 371 | 371 | 0.371
IT_AD1 | PROLIANT DL 360 G4p | 30-70% |  |  | 336 | 336 | 0.336
IT_AD2 | PROLIANT DL 360 G4p | 30-70% |  |  | 336 | 336 | 0.336
IT_OPSMANAGER | PROLIANT DL 360 G4p | 30-70% |  |  | 336 | 336 | 0.336
PRD_LDMS | PROLIANT DL 360 G4p | 30-70% |  |  | 336 | 336 | 0.336
PRD_ONFUSE | PROLIANT DL 360 G4p | 30-70% |  |  | 336 | 336 | 0.336
PRD_HRDB | PROLIANT DL 360 G4p | 30-70% |  |  | 336 | 336 | 0.336
PRD_HUDAD1 | PROLIANT DL 360 G4p | 30-70% |  |  | 336 | 336 | 0.336
PRD_HUDFTP | PROLIANT DL 360 G5 | 30-70% |  |  | 481 | 481 | 0.481
PRD_ECRMS | PROLIANT DL 360 G5 | 30-70% |  |  | 481 | 481 | 0.481
PRD_SL45BY | PROLIANT DL 360 G5 | 30-70% |  |  | 481 | 481 | 0.481
PRD_DUCTOR2 | PROLIANT DL 580 G2 | 30-70% |  |  | 715 | 715 | 0.715
PRD_YISQL2 | PROLIANT DL 580 G2 | 30-70% |  |  | 715 | 715 | 0.715
PRD_ICARE | PROLIANT ML 350 G4 | 30-70% |  |  | 572 | 572 | 0.572
PRD_JLDSD | PROLIANT DL 580 G2 | 30-70% |  |  | 715 | 715 | 0.715
PRD_HRES | PROLIANT ML 350 G3 | 30-70% |  |  | 513 | 513 | 0.513
PRD_GRAPHICS | PROLIANT ML 350 G4 | 30-70% |  |  | 572 | 572 | 0.572
IT_EXCHANGE | PROLIANT DL 360 G4p | 30-70% |  |  | 336 | 336 | 0.336
IT_VMWARE2 | PROLIANT ML 370 G3 | 50-80% |  |  | 590 | 590 | 0.59
PRD_PTHNAVG | PROLIANT ML 370 G3 | 30-70% |  |  | 572 | 572 | 0.572
PRD_FS1 | PROLIANT DL 380 G5 | 30-70% |  |  | 564 | 564 | 0.564
IT_VERITAS | PROLIANT DL 380 G5 | 30-70% |  |  | 564 | 564 | 0.564
PRD_INTRANET | PROLIANT DL 380 G5 | 50-80% |  |  | 658 | 658 | 0.658
IT_VMWARE1 | PROLIANT ML 570 G2 | 50-80% |  |  | 998 | 998 | 0.998
IT_SURFWATCH1 | PROLIANT DL 360 G5 | 30-70% |  |  | 481 | 481 | 0.481
IT_EXCHANGE2 | PROLIANT ML 370 G5 | 30-70% |  |  | 613 | 613 | 0.613
PRD_OSX | Xserve | 30-70% |  |  | 183 | 183 | 0.183
PRD_CITRIX | PROLIANT DL 360 G4p | 30-70% |  |  | 336 | 336 | 0.336
PRD_WILBR | PROLIANT DL 360 G4p | 30-70% |  |  | 336 | 336 | 0.336
PRD_AD | PROLIANT DL 360 G4p | 30-70% |  |  | 336 | 336 | 0.336
PRD_CLFS | PROLIANT DL 380 G4 | 30-70% |  |  | 478 | 478 | 0.478
PRD_RDI1 | PROLIANT DL 380 G5 | 30-70% |  |  | 564 | 564 | 0.564
PRD_PSLD10 | Sunfire E6900 | 30-70% |  |  | 9120 | 9120 | 9.12
PRD_PSLD20 | Sunfire E6900 | 30-70% |  |  | 9120 | 9120 | 9.12
PRD_PSLD30 | Sunfire E6900 | 30-70% |  |  | 9120 | 9120 | 9.12
PRD_PSLD40 | Sunfire E6900 | 30-70% |  |  | 9120 | 9120 | 9.12
PRD_SLUAT01 | Sunfire 420 | 30-70% |  |  | 610 | 610 | 0.61
PRD_SLUAT02 | Sunfire 420 | 30-70% |  |  | 610 | 610 | 0.61
PRD_SLWK10 | Sunfire E450 | 30-70% |  |  | 1664 | 1664 | 1.664
IT_CHDS1 | ProLiant DL360 G2 | 30-70% |  |  | 267 | 267 | 0.267
IT_HDS 9985 | Sun StorageTek 9985 | 50-80% |  |  | 1860 | 1860 | 1.86
PRD_2K3IPS01 | ProLiant DL360 G5 | 30-70% |  |  | 481 | 481 | 0.481
PRD_2K3IPS02 | ProLiant DL360 G5 | 30-70% |  |  | 481 | 481 | 0.481
PRD_2K3IPS03 | ProLiant DL360 G5 | 30-70% |  |  | 481 | 481 | 0.481
PRD_2K3IPS04 | ProLiant DL360 G5 | 30-70% |  |  | 481 | 481 | 0.481
PRD_W2KIPSSQM1 | ProLiant DL580 G2 | 30-70% |  |  | 715 | 715 | 0.715
PRD_2KIPSACT1 | ProLiant DL380 G3 | 30-70% |  |  | 564 | 564 | 0.564
PRD_2KIPSACT2 | ProLiant DL380 G3 | 30-70% |  |  | 564 | 564 | 0.564
IT_IPSSRV1 | ProLiant DL360 G4 | 30-70% |  |  | 336 | 336 | 0.336
PRD_2K3GISAG1 | ProLiant DL360 G4 | 50-80% |  |  | 336 | 336 | 0.336
PRD_2K3GISAG2 | ProLiant DL360 G4 | 50-80% |  |  | 336 | 336 | 0.336
PRD_2K3GISAPP1 | ProLiant DL360 G4 | 50-80% |  |  | 336 | 336 | 0.336
PRD_42K3GISWEB1 | ProLiant DL360 G4 | 30-70% |  |  | 336 | 336 | 0.336
PRD_42K3GISWEB2 | ProLiant DL360 G4 | 30-70% |  |  | 336 | 336 | 0.336
PRD_GISP03 | Sun Fire X4200 | 30-70% |  |  | 409 | 409 | 0.409
PRD_GISP04 | Sun Fire X4200 | 50-80% |  |  | 409 | 409 | 0.409
PRD_42K3WFAE1 | PROLIANT DL 380 G5 | 30-70% |  |  | 564 | 564 | 0.564
PRD_42K3WFAE2 | PROLIANT DL 380 G5 | 30-70% |  |  | 564 | 564 | 0.564
PRD_42K3WFCE | PROLIANT DL 380 G5 | 30-70% |  |  | 564 | 564 | 0.564
PRD_42K3WFPE | PROLIANT DL 380 G5 | 30-70% |  |  | 564 | 564 | 0.564
PRD_51K3WFPA | PROLIANT DL 380 G5 | 30-70% |  |  | 564 | 564 | 0.564
PRD_51LNXDB1 | PROLIANT DL 380 G5 | 30-70% |  |  | 564 | 564 | 0.564
PRD_51LNXDB2 | PROLIANT DL 380 G5 | 30-70% |  |  | 564 | 564 | 0.564
PRD_HSLD50 | Sun SPARC M5000 Srvr | 30-70% |  |  | 3198 | 3198 | 3.198
PRD_51K3IPSUAT01 | ProLiant DL360 G5 | 30-70% |  |  | 481 | 481 | 0.481
PRD_51PSUAT02 | ProLiant DL360 G5 | 30-70% |  |  | 481 | 481 | 0.481
PRD_51UATACT | ProLiant DL360 G5 | 30-70% |  |  | 481 | 481 | 0.481

## 4. Other Load Calculations
Other Existing Equipment Load Calculations | [7 empty] | Next Step >>>
Enter equipment information, along with Amps and Volts into the table below to calculate the total equipment load in kW for the data center. Where a power utility or calculation tool is not available from the vendor to express power requirements as kW, nameplate ratings are used to arrive at a kW input. This tool uses the following formula for this conversion: VOLT AMPS = AMPS x VOLTS WATTS = VOLT AMPS x 0.67 kW = WATTS/1000 List each equipment device located in the data center in the table below (other equipment includes switches, routers, etc.). Use nameplate ratings to collect amps and volts for each device to determine the kW required. Be sure to include the device name for tracking purposes.
Inputs |  |  |  |  | Outputs
Device Name | Type of Device | AMPS | VOLTS | WATTS (Enter if volts and amps are not available) | WATTS | kW | Total Existing Equipment Load (kW)
PRD_6509 | Cisco 6509 |  |  | 257 | 257 | 0.257 | 13.657
PRD_B2610 | Cisco 2610 | 1.5 | 240 |  | 360 | 0.36
PRD_3500 | Cisco 3500 |  |  | 1608 | 1608 | 1.608
PRD_ASA1 | Cisco 5510 |  |  | 150 | 150 | 0.15 | Average Equipment Load (kW)
PRD_A2610 | Cisco 2610 | 1.5 | 240 |  | 360 | 0.36
PRD_A3500 | Cisco 3500 |  |  | 1608 | 1608 | 1.608 | 0.14079
PRD_3750A | Cisco 3750-48TS |  |  | 75 | 75 | 0.075
PRD_DLRemote1 | Dlink DSS-24 |  |  | 49 | 49 | 0.049
PRD_DLRemote2 | Dlink DSS-24 |  |  | 49 | 49 | 0.049
IT_FATTY | FatPipe |  |  | 658 | 658 | 0.658
IT_KVM01 | Raitan Dominion KX464 |  |  | 29 | 29 | 0.029
IT_KVM03 | Raitan Dominion KX464 |  |  | 29 | 29 | 0.029
IT_KVM02 | Raitan Dominion KX464 |  |  | 29 | 29 | 0.029
IT_KVM04 | Raitan Dominion KX464 |  |  | 29 | 29 | 0.029
IT_KVM05 | Raitan Dominion KX464 |  |  | 29 | 29 | 0.029
IT_KVM07 | Raitan Dominion KX464 |  |  | 29 | 29 | 0.029
IT_KVMCLOSET1 | Raitan Dominion KX464 |  |  | 29 | 29 | 0.029
PRD_ADTRAN | Adtran Netvanta 3430 |  |  | 25 | 25 | 0.025
IT_6509 | Cisco 6509 |  |  | 257 | 257 | 0.257
PRD_ASA2 | Cisco 5510 |  |  | 150 | 150 | 0.15
PRD_C2610 | Cisco 2610 | 1.5 | 240 |  | 360 | 0.36
PRD_B3500 | Cisco 3500 |  |  | 1608 | 1608 | 1.608
APC Rack UPS x's 6 | Rackmounted UPS's |  |  | 5880 | 5880 | 5.88

## 5. Power Estimates
Server Room Power and Load Requirements Estimates |  |  |  | Next Step >>>
The following table summarizes the power load requirements for the organization's data center environment based on the inputs gathered in Tabs 1-3.
Item | Description | Subtotal kW | Total electrical service required from utility company in Amps
Power Requirement - Electrical |  |  | 1150.6151
Existing or actual equipment load | Ratings for servers and other equipment (calculated in Tab 3 and 4). | 92.4498
Estimated future loads | Based on the average server load and anticipated number of future servers to be added. | 45.2832 | Size of generator needed (estimated in kW)
Peak power draw from variation in critical loads | The total steady state load. Based on current and future loads. | 144.6196 | 535.0636
UPS inefficiency and battery charging | Actual and future loads (kW). | 44.0745
Lighting | Based on the floor area in the server room. | 2.4 | Electrical service required from utility company in Amps per sq. ft
Total power required to support electrical demands | Power drawn from servers, equipment, UPS, and lighting. | 191.0941
Power Requirement - Cooling |  |  | 0.95885
Power to support chiller system | Based on the standard assumption that power required is 70% of total electrical demand. | N/A
Power to support DX system | Based on the standard assumption that power required is 100% of total electrical demand. | 191.0941
Total power required to support cooling demands | Power drawn from cooling devices. | 191.0941
Total Power Requirement
Total amount of power required to support both electrical and cooling demands | Total amount of power required that includes current and future needs for power and cooling. | 382.1883
Size of Electrical Service Estimate
Regulator (i.e.NEC) requirements | Total electrical and cooling requirements multiplied by 1.25 to meet regulator's requirements. | 477.7354
Three phase AC voltage | Existing AC voltage from building (can be found at service entrance). | 240
Electrical service required from utility company (calculated in Amps) | Utility company estimate. | 1150.6151
Size of Standby Generator Estimate (if Applicable)
Critical loads that require generator backup | Based on total power to support electrical demand. | 248.4224
Cooling loads that require generator backup | Based on total power to support cooling. | 286.6412
Estimated size of generator required |  | 535.0636

## 6. Cooling Estimates
Cooling Requirements Estimation |  |  |  | Next Step >>>
The following table summarizes the cooling load requirements for the organization's data center environment.
Item | Description | Watts | BTUs per Hour
Total existing server and storage load | Total heat given off from server and storage devices in the data center. | 78792.76 | 268683.3116
Total existing equipment load | Total heat given off from other equipment located in the data center. | 13657 | 46570.37
Estimated future loads | The amount of heat given off from expected future devices to be added in the data center. | 45283.1954 | 154415.6963
UPS inefficiency and battery charging | Total heat given off from the UPS or backup battery located in the data center. | 44074.5457 | 150294.2009
Power Distribution (PDU) | Total heat given off from the power distribution unit located in the data center. | 2756.5691 | 9399.9007
Lighting | Amount of heat given off from lighting in the data center. Based on the total amount of floor area in the data center. (2.0 x Floor Area in sq. ft.) | 2400 | 8184
People | Amount of heat given off from the maximum number of employees working in the data center. | 500 | 1705
Total Estimated Cooling Load | The total size of cooling load required to cool the data center. | 187464.0702 | 639252.4795
Total Estimated Cooling Load (in Tons) | The required sizing for a cooling device measured in tons based on the total estimated cooling load/heat output. | 53.271 | TONS

## 7. Standby Power Estimates
Standby Power Requirements Estimation |  |  | Next Step >>>
The following table summarizes the standby power load requirements for the organizations' data center environment.
Item | Description | kW
Server load power requirements | Total estimated power requirements for servers and storage devices located in the data center. | 78.7928
Other equipment power requirements | Total estimated power requirements for other equipment (routers, computers, switches, convenience plugs etc.) located in the data center. | 13.657
Estimated future load requirements | Based on the average server load and anticipated number of future servers to be added. | 45.2832
Cooling load requirements | Total size of cooling load required to cool the data center based on the total heat output. | 187.4641
Emergency lighting power load | Total load required to power emergency lighting in response to an outage. | 2.4
Total size of load requiring standby power | Total load that will require a standby power supply in the event of an outage. | 327.597

## 8. Results Summary
Data Center Requirements Estimates Results Summary
The following table summarizes the complete results from Tabs 1 - 4 that estimate the organization's critical power, cooling, and standby power requirements for the data center.
Item | Description | Total | Unit
Power Requirements Results Summary
Total Existing Server Load | Total power load required to support the data center's servers. | 78.7928 | kW
Average Server Load | Average power load per server in the data center. | 0.90566 | kW
Total Existing Equipment Load | Total power load required to support other equipment in the data center. | 13.657 | kW
Average Equipment Load | Average power load per piece of other equipment in the data center. | 0.14079 | kW
Total Electrical Service Required From Utility Company in Amps | Power to be requested from the utility company to aid in budgeting. | 1150.6151 | Amps
Total Electrical Service Required From Utility Company in Amps per Sq. Ft | Power to be requested from the utility company per square foot in the data center to aid in budgeting. | 0.95885 | Amps
Size of Generator Needed | Size of generator required to support server and other equipment as backup power. | 535.0636 | kW
Cooling Requirements Results Summary
Total estimated cooling load (BTUs/Hr) | The total size of cooling load required to cool the data center based on the total heat output. | 639252.4795 | BTUs
Size of cooling device required (in tons) | The required sizing for a cooling device measured in tons required to cool the data center based on the total estimated cooling load/heat output. | 53.271 | Tons
BTUs per square foot | The amount of cooling required per square foot in the data center. | 532.7104 | Sq. ft
Number of 20-ton air conditioners required | Cooling requirements distributed amongst 20-ton air handlers for the data center. If the number is not a whole number, it shoud lbe rounded up to the nearest whole number. | 2.6636 | AC Units
Standby Power Requirements Results Summary
Total data center load requiring standby power | Total load that will require a standby power supply in the event of an outage. | 327.597 | kW
Over sizing for backup power at 75% | Over sizing for future load requirements with an additional 75% standby power supply. | 245.6978 | kW
UPS requirements | Amount of load requiring a UPS system. | 573.2948 | kW
Generator required in kW | Size of generator required to power data center in case of an outage. kVA calculations take a power factor of 0.8 into account. | 573.2948 | kW
Generator required in kVA | Size of generator required to power data center in case of an outage. kVA calculations take a power factor of 0.8 into account. | 687.9538 | kVA

## Hidden Calcs (hidden)
| TAB 3 - Server Load Calculations | [10 empty] | TAB 4 - Other Load Calculations | [8 empty] | TAB 5 - Power Estimates |  | TAB 8 - Results Summary |  | Tab 6 - Cooling requirements |  |  |  | Tab 7 - Standby Power Estimates
[23 empty] | POWER |  | INPUTS |  |  |  | INPUTS
| Inputs | [5 empty] | Calcs |  | Total | Average |  | Inputs |  |  |  |  | Outputs |  | Total | Average |  |  | Total Existing Server Load | 78.7928 | Input Table 1. Info-Tech Power Tool Calculator |  |  |  | Table 1. Inputs from Info-Tech Power Requirements Calculator
| Device Name | Server Model | Utilization Assumption | AMPS | VOLTS | WATTS | WATTS | kW | 78.7928 | 0.90566 |  | Device Name | Type of Device? | AMPS | VOLTS | Watts | WATTS | kW | 13.657 | 0.14079 | INPUT |  | Average Server Load | 0.90566 | Item | Description | Kw |  | Item | Description | kW
1 | IT_NETPRO | PROLIANT DL 360 G4p | 30-70% | 1.2 | 240 | 0 | 192.96 | 0.19296 |  |  | 1 | PRD_6509 | Cisco 6509 | 0 | 0 | 257 | 257 | 0.257 |  |  | #REF! | 1200 | Total Existing Equipment Load | 13.657 | Total existing server and storage load | Total estimated power requirements for servers and storage devices located in the data center. | 78.7928 |  | Server load power requirements | Total estimated power requirements for servers and storage devices located in the data center. | 78.7928
2 | IT_SURFWATCH | PROLIANT DL 360 G2 | 30-70% | 5 | 48 | 0 | 160.8 | 0.1608 |  |  | 2 | PRD_B2610 | Cisco 2610 | 1.5 | 240 | 0 | 360 | 0.36 |  |  | #REF! | 50 | Average Equipment Load | 0.14079 | Total existing equipment load | Total estimated power requirements for other equipment (routers, computers, switches, etc.) located in the data center. | 13.657 |  | Other equipment power requirements | Total estimated power requirements for other equipment (routers, computers, switches etc.) located in the data center. | 13.657
3 | PRD_CITRIX02 | PROLIANT BL 20P G2 | 30-70% | 0 | 0 | 684 | 684 | 0.684 |  |  | 3 | PRD_3500 | Cisco 3500 | 0 | 0 | 1608 | 1608 | 1.608 |  |  | #REF! | DX System | Total Electrical Service Required From Utility Company in Amps | 1150.6151 | Estimated future loads | The number of expected server and storage devices to be added over the lifespan of the data center. This number is based on the average server load and multiplied by the anticipated number of future servers to be added. | 45.2832 |  | Estimated Future load requirements | Based on the average server load and anticipated number of future servers to be added. | 45.2832
4 | PRD_CITRIX03 | PROLIANT BL 20P G2 | 30-70% | 0 | 0 | 684 | 684 | 0.684 |  |  | 4 | PRD_ASA1 | Cisco 5510 | 0 | 0 | 150 | 150 | 0.15 |  |  | #REF! | 240 | Total Electrical Service Required From Utility Company in Amps per Sq. Ft | 0.95885 | UPS inefficiency and battery charging | Based on backup for current and future loads. If the UPS is not located in the data center, enter a value of zero. | 44.0745
5 | PRD_CITRIX01 | PROLIANT BL 20P G2 | 30-70% | 0 | 0 | 684 | 684 | 0.684 |  |  | 5 | PRD_A2610 | Cisco 2610 | 1.5 | 240 | 0 | 360 | 0.36 |  |  |  |  | Size of Generator Needed | 535.0636 |  |  |  |  | Table 2. Inputs from Info-Tech Cooling Requirements Calculator
6 | PRD_CITRIX04 | PROLIANT DL 360 G4p | 30-70% | 0 | 0 | 336 | 336 | 0.336 |  |  | 6 | PRD_A3500 | Cisco 3500 | 0 | 0 | 1608 | 1608 | 1.608 | [6 empty] | Input Table 2. Other Inputs |  |  |  | Item | Description | Watts
7 | IT_DEVELOPMENT1 | PROLIANT DL 320 G2 | 30-70% | 0 | 0 | 251 | 251 | 0.251 |  |  | 7 | PRD_3750A | Cisco 3750-48TS | 0 | 0 | 75 | 75 | 0.075 |  | DX System | Item |  | COOLING |  | Item | Description | Number |  | Cooling load requirements | The total size of cooling load required to cool the data center based on the total heat output. | 187464.0702
8 | IT_REMOTEACCESS | PROLIANT DL 320 G2 | 30-70% | 0 | 0 | 251 | 251 | 0.251 |  |  | 8 | PRD_DLRemote1 | Dlink DSS-24 | 0 | 0 | 49 | 49 | 0.049 |  | Chiller System | Power Requirement - Electrical |  | Total estimated cooling load (BTUs/Hr) | 639252.4795 | Total floor area in the data center (sq. ft) | The total floor area of the data center in square feet. | 1200
9 | IT_SOURCESAFE | PROLIANT DL 320 G2 | 30-70% | 0 | 0 | 251 | 251 | 0.251 |  |  | 9 | PRD_DLRemote2 | Dlink DSS-24 | 0 | 0 | 49 | 49 | 0.049 |  |  | Existing or actual equipment load | 92.4498 | Size of cooling device required (in tons) | 53.271 | Maximum number of people in the data center | People that will be consistently working within the data center. A maximum number should be used to account for intermittent personnel and air exchange. | 5 |  | Table 3. Other Inputs
10 | IT_BESDMZ | PROLIANT DL 320 G2 | 30-70% | 0 | 0 | 251 | 251 | 0.251 |  |  | 10 | IT_FATTY | FatPipe | 0 | 0 | 658 | 658 | 0.658 |  |  | Estimated future loads | 45.2832 | BTUs per square foot | 532.7104 | Power distribution rating (Watts) | Total power drawn from the power distribution unit in Watts. | 191 |  | Item | Description | Sq. Ft
11 | IT_AVTECH | PROLIANT DL 320 G2 | 30-70% | 0 | 0 | 251 | 251 | 0.251 |  |  | 11 | IT_KVM01 | Raitan Dominion KX464 | 0 | 0 | 29 | 29 | 0.029 |  |  | Peak power draw from variation in critical loads | 144.6196 | Number of 20-ton air conditioners required | 2.6636 |  |  |  |  | Total data center floor space (sq.ft) | The total floor area of the data center in square feet. | 1200
12 | IT_SYNCSORT | PROLIANT DL 320 | 30-70% | 0 | 0 | 171 | 171 | 0.171 |  |  | 12 | IT_KVM03 | Raitan Dominion KX464 | 0 | 0 | 29 | 29 | 0.029 |  |  | UPS inefficiency and battery charging | 44.0745 |  |  | Calculations
13 | PRD_MOBILEAPPS | PROLIANT DL 320 G2 | 30-70% | 0 | 0 | 251 | 251 | 0.251 |  |  | 13 | IT_KVM02 | Raitan Dominion KX464 | 0 | 0 | 29 | 29 | 0.029 |  |  | Lighting | 2.4 | STANDBY POWER | [5 empty] | Calculations
14 | PRD_ANTGY | PROLIANT DL 320 G5 | 30-70% | 0 | 0 | 194 | 194 | 0.194 |  |  | 14 | IT_KVM04 | Raitan Dominion KX464 | 0 | 0 | 29 | 29 | 0.029 |  |  | Total power required to support electrical demands | 191.0941 | Total data center load requiring standby power | 327.597 | Item | Description | Watts | BTUs per Hour
15 | PRD_ACCOUNTFND | PROLIANT DL 360 G2 | 30-70% | 0 | 0 | 267 | 267 | 0.267 |  |  | 15 | IT_KVM05 | Raitan Dominion KX464 | 0 | 0 | 29 | 29 | 0.029 |  |  | Power Requirement - Cooling |  | Over sizing for backup power at 75% | 245.6978 | Total existing server and storage load | Total heat given off from server and storage devices in the data center. | 78792.76 | 268683.3116 | Item | Description | kW
16 | PRD_SCHEDULELEADS | PROLIANT DL 360 G2 | 30-70% | 0 | 0 | 267 | 267 | 0.267 |  |  | 16 | IT_KVM07 | Raitan Dominion KX464 | 0 | 0 | 29 | 29 | 0.029 |  |  | Power to support chiller system | N/A | UPS requirements | 573.2948 | Total existing equipment load | Total heat given off from other equipment located in the data center. | 13657 | 46570.37 | Server load power requirements | Total estimated power requirements for servers and storage devices located in the data center. | 78.7928
17 | IT_SURFWATCH | PROLIANT DL 360 G2 | 30-70% | 0 | 0 | 267 | 267 | 0.267 |  |  | 17 | IT_KVMCLOSET1 | Raitan Dominion KX464 | 0 | 0 | 29 | 29 | 0.029 |  |  | Power to support DX system | 191.0941 | Generator required in kW | 573.2948 | Estimated future loads | The amount of heat given off from expected future devices to be added in the data center. | 45283.1954 | 154415.6963 | Other equipment power requirements | Total estimated power requirements for other equipment (routers, computers, switches, convenience plugs etc.) located in the data center. | 13.657
18 | IT_EDIRECTORY | PROLIANT DL 360 G2 | 30-70% | 0 | 0 | 267 | 267 | 0.267 |  |  | 18 | PRD_ADTRAN | Adtran Netvanta 3430 | 0 | 0 | 25 | 25 | 0.025 |  |  | Total power required to support cooling demands | 191.0941 | Generator required in kVA | 687.9538 | UPS inefficiency and battery charging | Total heat given off from the UPS or backup battery located in the data center. | 44074.5457 | 150294.2009 | Estimated Future load requirements | Based on the average server load and anticipated number of future servers to be added. | 45.2832
19 | PRD_FAS1 | PROLIANT DL 360 G3 | 30-70% | 0 | 0 | 373 | 373 | 0.373 |  |  | 19 | IT_6509 | Cisco 6509 | 0 | 0 | 257 | 257 | 0.257 |  |  | Total Power Requirement |  |  |  | Power Distribution (PDU) | Total heat given off from the power distribution unit located in the data center. | 2756.5691 | 9399.9007 | Cooling load requirements | Total size of cooling load required to cool the data center based on the total heat output. | 187.4641
20 | PRD_BES1 | PROLIANT DL 360 G5 | 30-70% | 0 | 0 | 481 | 481 | 0.481 |  |  | 20 | PRD_ASA2 | Cisco 5510 | 0 | 0 | 150 | 150 | 0.15 |  |  | Total amount of power required to support both electrical and cooling demands | 382.1883 |  |  | Lighting | Amount of heat given off from lighting in the data center. Based on the total amount of floor area in the data center. (2.0 x Floor Area in sq. ft.) | 2400 | 8184 | Emergency lighting power load | Total load required to power emergency lighting in response to an outage. | 2.4
21 | IT_LDDHCP1 | PROLIANT DL 360 G3 | 30-70% | 0 | 0 | 371 | 371 | 0.371 |  |  | 21 | PRD_C2610 | Cisco 2610 | 1.5 | 240 | 0 | 360 | 0.36 |  |  | Size of Electrical Service Estimate |  |  |  | People | Amount of heat given off from the maximum number of employees working in the data center. | 500 | 1705 | Total size of load requiring standby power | Total load that will require a standby power supply in the event of an outage. | 327.597
22 | IT_AD1 | PROLIANT DL 360 G4p | 30-70% | 0 | 0 | 336 | 336 | 0.336 |  |  | 22 | PRD_B3500 | Cisco 3500 | 0 | 0 | 1608 | 1608 | 1.608 |  |  | Regulator (i.e.NEC) requirements | 477.7354 |  |  | Total Estimated Cooling Load | The total size of cooling load required to cool the data center. | 187464.0702 | 639252.4795
23 | IT_AD2 | PROLIANT DL 360 G4p | 30-70% | 0 | 0 | 336 | 336 | 0.336 |  |  | 23 | APC Rack UPS x's 6 | Rackmounted UPS's | 0 | 0 | 5880 | 5880 | 5.88 |  |  | Three phase AC voltage | 240 |  |  |  | The required sizing for a cooling device measured in tons based on the total estimated cooling load/heat output.
24 | IT_OPSMANAGER | PROLIANT DL 360 G4p | 30-70% | 0 | 0 | 336 | 336 | 0.336 |  |  | 24 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Electrical service required from utility company (calculated in Amps) | 1150.6151 |  |  | Total Estimated Cooling Load (in Tons) |  |  | 53.271
25 | PRD_LDMS | PROLIANT DL 360 G4p | 30-70% | 0 | 0 | 336 | 336 | 0.336 |  |  | 25 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Size of Standby Generator Estimate (if Applicable)
26 | PRD_ONFUSE | PROLIANT DL 360 G4p | 30-70% | 0 | 0 | 336 | 336 | 0.336 |  |  | 26 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Critical loads that require generator backup | 248.4224
27 | PRD_HRDB | PROLIANT DL 360 G4p | 30-70% | 0 | 0 | 336 | 336 | 0.336 |  |  | 27 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Cooling loads that require generator backup | 286.6412
28 | PRD_HUDAD1 | PROLIANT DL 360 G4p | 30-70% | 0 | 0 | 336 | 336 | 0.336 |  |  | 28 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Estimated size of generator required | 535.0636
29 | PRD_HUDFTP | PROLIANT DL 360 G5 | 30-70% | 0 | 0 | 481 | 481 | 0.481 |  |  | 29 | 0 | 0 | 0 | 0 | 0
30 | PRD_ECRMS | PROLIANT DL 360 G5 | 30-70% | 0 | 0 | 481 | 481 | 0.481 |  |  | 30 | 0 | 0 | 0 | 0 | 0
31 | PRD_SL45BY | PROLIANT DL 360 G5 | 30-70% | 0 | 0 | 481 | 481 | 0.481 |  |  | 31 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Electrical service required from utility company in Amps per sq. ft
32 | PRD_DUCTOR2 | PROLIANT DL 580 G2 | 30-70% | 0 | 0 | 715 | 715 | 0.715 |  |  | 32 | 0 | 0 | 0 | 0 | 0
33 | PRD_YISQL2 | PROLIANT DL 580 G2 | 30-70% | 0 | 0 | 715 | 715 | 0.715 |  |  | 33 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 0.95885
34 | PRD_ICARE | PROLIANT ML 350 G4 | 30-70% | 0 | 0 | 572 | 572 | 0.572 |  |  | 34 | 0 | 0 | 0 | 0 | 0
35 | PRD_JLDSD | PROLIANT DL 580 G2 | 30-70% | 0 | 0 | 715 | 715 | 0.715 |  |  | 35 | 0 | 0 | 0 | 0 | 0
36 | PRD_HRES | PROLIANT ML 350 G3 | 30-70% | 0 | 0 | 513 | 513 | 0.513 |  |  | 36 | 0 | 0 | 0 | 0 | 0
37 | PRD_GRAPHICS | PROLIANT ML 350 G4 | 30-70% | 0 | 0 | 572 | 572 | 0.572 |  |  | 37 | 0 | 0 | 0 | 0 | 0
38 | IT_EXCHANGE | PROLIANT DL 360 G4p | 30-70% | 0 | 0 | 336 | 336 | 0.336 |  |  | 38 | 0 | 0 | 0 | 0 | 0
39 | IT_VMWARE2 | PROLIANT ML 370 G3 | 50-80% | 0 | 0 | 590 | 590 | 0.59 |  |  | 39 | 0 | 0 | 0 | 0 | 0
40 | PRD_PTHNAVG | PROLIANT ML 370 G3 | 30-70% | 0 | 0 | 572 | 572 | 0.572 |  |  | 40 | 0 | 0 | 0 | 0 | 0
41 | PRD_FS1 | PROLIANT DL 380 G5 | 30-70% | 0 | 0 | 564 | 564 | 0.564 |  |  | 41 | 0 | 0 | 0 | 0 | 0
42 | IT_VERITAS | PROLIANT DL 380 G5 | 30-70% | 0 | 0 | 564 | 564 | 0.564 |  |  | 42 | 0 | 0 | 0 | 0 | 0
43 | PRD_INTRANET | PROLIANT DL 380 G5 | 50-80% | 0 | 0 | 658 | 658 | 0.658 |  |  | 43 | 0 | 0 | 0 | 0 | 0
44 | IT_VMWARE1 | PROLIANT ML 570 G2 | 50-80% | 0 | 0 | 998 | 998 | 0.998 |  |  | 44 | 0 | 0 | 0 | 0 | 0
45 | IT_SURFWATCH1 | PROLIANT DL 360 G5 | 30-70% | 0 | 0 | 481 | 481 | 0.481 |  |  | 45 | 0 | 0 | 0 | 0 | 0
46 | IT_EXCHANGE2 | PROLIANT ML 370 G5 | 30-70% | 0 | 0 | 613 | 613 | 0.613 |  |  | 46 | 0 | 0 | 0 | 0 | 0
47 | PRD_OSX | Xserve | 30-70% | 0 | 0 | 183 | 183 | 0.183 |  |  | 47 | 0 | 0 | 0 | 0 | 0
48 | PRD_CITRIX | PROLIANT DL 360 G4p | 30-70% | 0 | 0 | 336 | 336 | 0.336 |  |  | 48 | 0 | 0 | 0 | 0 | 0
49 | PRD_WILBR | PROLIANT DL 360 G4p | 30-70% | 0 | 0 | 336 | 336 | 0.336 |  |  | 49 | 0 | 0 | 0 | 0 | 0
50 | PRD_AD | PROLIANT DL 360 G4p | 30-70% | 0 | 0 | 336 | 336 | 0.336 |  |  | 50 | 0 | 0 | 0 | 0 | 0
51 | PRD_CLFS | PROLIANT DL 380 G4 | 30-70% | 0 | 0 | 478 | 478 | 0.478 |  |  | 51 | 0 | 0 | 0 | 0 | 0
52 | PRD_RDI1 | PROLIANT DL 380 G5 | 30-70% | 0 | 0 | 564 | 564 | 0.564 |  |  | 52 | 0 | 0 | 0 | 0 | 0
53 | PRD_PSLD10 | Sunfire E6900 | 30-70% | 0 | 0 | 9120 | 9120 | 9.12 |  |  | 53 | 0 | 0 | 0 | 0 | 0
54 | PRD_PSLD20 | Sunfire E6900 | 30-70% | 0 | 0 | 9120 | 9120 | 9.12 |  |  | 54 | 0 | 0 | 0 | 0 | 0
55 | PRD_PSLD30 | Sunfire E6900 | 30-70% | 0 | 0 | 9120 | 9120 | 9.12 |  |  | 55 | 0 | 0 | 0 | 0 | 0
56 | PRD_PSLD40 | Sunfire E6900 | 30-70% | 0 | 0 | 9120 | 9120 | 9.12 |  |  | 56 | 0 | 0 | 0 | 0 | 0
57 | PRD_SLUAT01 | Sunfire 420 | 30-70% | 0 | 0 | 610 | 610 | 0.61 |  |  | 57 | 0 | 0 | 0 | 0 | 0
58 | PRD_SLUAT02 | Sunfire 420 | 30-70% | 0 | 0 | 610 | 610 | 0.61 |  |  | 58 | 0 | 0 | 0 | 0 | 0
59 | PRD_SLWK10 | Sunfire E450 | 30-70% | 0 | 0 | 1664 | 1664 | 1.664 |  |  | 59 | 0 | 0 | 0 | 0 | 0
60 | IT_CHDS1 | ProLiant DL360 G2 | 30-70% | 0 | 0 | 267 | 267 | 0.267 |  |  | 60 | 0 | 0 | 0 | 0 | 0
61 | IT_HDS 9985 | Sun StorageTek 9985 | 50-80% | 0 | 0 | 1860 | 1860 | 1.86 |  |  | 61 | 0 | 0 | 0 | 0 | 0
62 | PRD_2K3IPS01 | ProLiant DL360 G5 | 30-70% | 0 | 0 | 481 | 481 | 0.481 |  |  | 62 | 0 | 0 | 0 | 0 | 0
63 | PRD_2K3IPS02 | ProLiant DL360 G5 | 30-70% | 0 | 0 | 481 | 481 | 0.481 |  |  | 63 | 0 | 0 | 0 | 0 | 0
64 | PRD_2K3IPS03 | ProLiant DL360 G5 | 30-70% | 0 | 0 | 481 | 481 | 0.481 |  |  | 64 | 0 | 0 | 0 | 0 | 0
65 | PRD_2K3IPS04 | ProLiant DL360 G5 | 30-70% | 0 | 0 | 481 | 481 | 0.481 |  |  | 65 | 0 | 0 | 0 | 0 | 0
66 | PRD_W2KIPSSQM1 | ProLiant DL580 G2 | 30-70% | 0 | 0 | 715 | 715 | 0.715 |  |  | 66 | 0 | 0 | 0 | 0 | 0
67 | PRD_2KIPSACT1 | ProLiant DL380 G3 | 30-70% | 0 | 0 | 564 | 564 | 0.564 |  |  | 67 | 0 | 0 | 0 | 0 | 0
68 | PRD_2KIPSACT2 | ProLiant DL380 G3 | 30-70% | 0 | 0 | 564 | 564 | 0.564 |  |  | 68 | 0 | 0 | 0 | 0 | 0
69 | IT_IPSSRV1 | ProLiant DL360 G4 | 30-70% | 0 | 0 | 336 | 336 | 0.336 |  |  | 69 | 0 | 0 | 0 | 0 | 0
70 | PRD_2K3GISAG1 | ProLiant DL360 G4 | 50-80% | 0 | 0 | 336 | 336 | 0.336 |  |  | 70 | 0 | 0 | 0 | 0 | 0
71 | PRD_2K3GISAG2 | ProLiant DL360 G4 | 50-80% | 0 | 0 | 336 | 336 | 0.336 |  |  | 71 | 0 | 0 | 0 | 0 | 0
72 | PRD_2K3GISAPP1 | ProLiant DL360 G4 | 50-80% | 0 | 0 | 336 | 336 | 0.336 |  |  | 72 | 0 | 0 | 0 | 0 | 0
73 | PRD_42K3GISWEB1 | ProLiant DL360 G4 | 30-70% | 0 | 0 | 336 | 336 | 0.336 |  |  | 73 | 0 | 0 | 0 | 0 | 0
74 | PRD_42K3GISWEB2 | ProLiant DL360 G4 | 30-70% | 0 | 0 | 336 | 336 | 0.336 |  |  | 74 | 0 | 0 | 0 | 0 | 0
75 | PRD_GISP03 | Sun Fire X4200 | 30-70% | 0 | 0 | 409 | 409 | 0.409 |  |  | 75 | 0 | 0 | 0 | 0 | 0
76 | PRD_GISP04 | Sun Fire X4200 | 50-80% | 0 | 0 | 409 | 409 | 0.409 |  |  | 76 | 0 | 0 | 0 | 0 | 0
77 | PRD_42K3WFAE1 | PROLIANT DL 380 G5 | 30-70% | 0 | 0 | 564 | 564 | 0.564 |  |  | 77 | 0 | 0 | 0 | 0 | 0
78 | PRD_42K3WFAE2 | PROLIANT DL 380 G5 | 30-70% | 0 | 0 | 564 | 564 | 0.564 |  |  | 78 | 0 | 0 | 0 | 0 | 0
79 | PRD_42K3WFCE | PROLIANT DL 380 G5 | 30-70% | 0 | 0 | 564 | 564 | 0.564 |  |  | 79 | 0 | 0 | 0 | 0 | 0
80 | PRD_42K3WFPE | PROLIANT DL 380 G5 | 30-70% | 0 | 0 | 564 | 564 | 0.564 |  |  | 80 | 0 | 0 | 0 | 0 | 0
81 | PRD_51K3WFPA | PROLIANT DL 380 G5 | 30-70% | 0 | 0 | 564 | 564 | 0.564 |  |  | 81 | 0 | 0 | 0 | 0 | 0
82 | PRD_51LNXDB1 | PROLIANT DL 380 G5 | 30-70% | 0 | 0 | 564 | 564 | 0.564 |  |  | 82 | 0 | 0 | 0 | 0 | 0
83 | PRD_51LNXDB2 | PROLIANT DL 380 G5 | 30-70% | 0 | 0 | 564 | 564 | 0.564 |  |  | 83 | 0 | 0 | 0 | 0 | 0
84 | PRD_HSLD50 | Sun SPARC M5000 Srvr | 30-70% | 0 | 0 | 3198 | 3198 | 3.198 |  |  | 84 | 0 | 0 | 0 | 0 | 0
85 | PRD_51K3IPSUAT01 | ProLiant DL360 G5 | 30-70% | 0 | 0 | 481 | 481 | 0.481 |  |  | 85 | 0 | 0 | 0 | 0 | 0
86 | PRD_51PSUAT02 | ProLiant DL360 G5 | 30-70% | 0 | 0 | 481 | 481 | 0.481 |  |  | 86 | 0 | 0 | 0 | 0 | 0
87 | PRD_51UATACT | ProLiant DL360 G5 | 30-70% | 0 | 0 | 481 | 481 | 0.481 |  |  | 87 | 0 | 0 | 0 | 0 | 0
88 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 88 | 0 | 0 | 0 | 0 | 0
89 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 89 | 0 | 0 | 0 | 0 | 0
90 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 90 | 0 | 0 | 0 | 0 | 0
91 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 91 | 0 | 0 | 0 | 0 | 0
92 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 92 | 0 | 0 | 0 | 0 | 0
93 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 93 | 0 | 0 | 0 | 0 | 0
94 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 94 | 0 | 0 | 0 | 0 | 0
95 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 95 | 0 | 0 | 0 | 0 | 0
[11 empty] | 96 | 0 | 0 | 0 | 0 | 0
| 87 | [9 empty] | 97 | 0 | 0 | 0 | 0 | 0
[11 empty] | 98 | 0 | 0 | 0 | 0 | 0
[11 empty] | 99 | 0 | 0 | 0 | 0 | 0
[11 empty] | 100 | 0 | 0 | 0 | 0 | 0
[11 empty] | 101 | 0 | 0 | 0 | 0 | 0
23